## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest1					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	2000					Gross Wall	2000
North Window	20		15		300		Windows	70		Single	80	5600
South Window	20		25		500		Doors			Single	80	0
East/West Window	20		45		900		Net Wall	1927		No Insulation	18	34686
Sky-Lite	10		139		1390		Ceiling	3000		No Insulation	21	63000
Doors	3		11		33		Floor	3000		Base – No Ins.	4	12000
Net Wall	1927		No Insulation	4	7708		Infiltration	Area	3000	¼ Air Change	0.32	9600
Ceiling	3000		No Insulation	11	33000			Ht.	10
Floor	3000		No Insulation	4	12000		Heat Loss Subtotal					124886
Infiltration	Area	3000	¼ Air Change	0.068	2040		Total Loss	124886		1.25		156107.5
	Ht.	10
People	2		300		600
Appliance	500				500		Notes:
Subtotal					58971
Duct Loss	58971		0.05		2948.55
Total Sensible					61919.55
Latent Infiltration	Area	3000	¼ Air Change	0.065	1950
	Ht.	10
People	2		230		460
Total Latent					2410
Total Gain	61919.55		2410		64329.55

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1