## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest7					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	90					Gross Wall	90
North Window	1		15		15		Windows	4		Single	80	320
South Window	1		25		25		Doors			Single	80	0
East/West Window	1		45		45		Net Wall	85		6 Inches	4	340
Sky-Lite	1		139		139		Ceiling	5		10 Inches	2	10
Doors	1		11		11		Floor	5		Crawl Space	21	105
Net Wall	85		3 Inches	1.5	127.5		Infiltration	Area	111	½ Air Change	0.63	629.37
Ceiling	5		10 Inches	1.3	6.5			Ht.	9
Floor	5		6 Inches	0.5	2.5		Heat Loss Subtotal					1404.37
Infiltration	Area	111	½ Air Change	0.137	136.863		Total Loss	1404.37		1.25		1755.4625
	Ht.	9
People	1		300		300
Appliance	1000				1000		Notes:
Subtotal					1808.363
Duct Loss	1808.363		0.05		90.41815
Total Sensible					1898.78115
Latent Infiltration	Area	111	½ Air Change	0.13	129.87
	Ht.	9
People	1		230		230
Total Latent					359.87
Total Gain	1898.78115		359.87		2258.65115

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1