## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest3					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	100					Gross Wall	100
North Window	10		15		150		Windows	65		Triple	23	1495
South Window	30		25		750		Doors			Triple	23	0
East/West Window	15		45		675		Net Wall	30		6 Inches	4	120
Sky-Lite	10		139		1390		Ceiling	155		10 Inches	2	310
Doors	5		11		55		Floor	155		Bsmt. – 3 Inches	2	310
Net Wall	30		3 Inches	1.5	45		Infiltration	Area	155	1 Air Change	1.26	1171.8
Ceiling	155		10 Inches	1.3	201.5			Ht.	6
Floor	155		6 Inches	0.5	77.5		Heat Loss Subtotal					3406.8
Infiltration	Area	155	1 Air Change	0.275	255.75		Total Loss	3406.8		1		3406.8
	Ht.	6
People	20		300		6000
Appliance	1500				1500		Notes:
Subtotal					11099.75
Duct Loss	11099.75		0.05		554.9875
Total Sensible					11654.7375
Latent Infiltration	Area	155	1 Air Change	0.26	241.8
	Ht.	6
People	20		230		4600
Total Latent					4841.8
Total Gain	11654.7375		4841.8		16496.5375

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1