## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest3					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	100					Gross Wall	100
North Window	10		15		150		Windows	65		Triple	23	1495
South Window	30		25		750		Doors	5		Triple	23	115
East/West Window	15		45		675		Net Wall	30		3 Inches	5	150
Sky-Lite	10		139		1390		Ceiling	155		10 Inches	2	310
Doors	5		11		55		Floor	155		Bsmt. – 3 Inches	2	310
Net Wall	30		3 Inches	1.5	45		Infiltration	Area	155	1 Air Change	1.26	1171.8
Ceiling	155		10 Inches	1.3	201.5			Ht.	6
Floor	155		6 Inches	0.5	77.5		Heat Loss Subtotal					3551.8
Infiltration	Area	155	1 Air Change	0.275	255.75		Total Loss	3551.8		1		3551.8
	Ht.	6
People	20		300		6000
Appliance	1500				1500		Notes:
Subtotal					11099.75
Duct Loss	11099.75		0.05		554.9875
Total Sensible					11654.7375
Latent Infiltration	Area	155	1 Air Change	0.26	241.8
	Ht.	6
People	20		230		4600
Total Latent					4841.8
Total Gain	11654.7375		4841.8		16496.5375

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1