## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest4					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	5000					Gross Wall	5000
North Window	100		15		1500		Windows	1850		Single	80	148000
South Window	250		25		6250		Doors	1		Single	80	80
East/West Window	1000		45		45000		Net Wall	3149		No Insulation	18	56682
Sky-Lite	500		139		69500		Ceiling	2500		No Insulation	21	52500
Doors	1		11		11		Floor	5000		Crawl Space	21	105000
Net Wall	3149		No Insulation	4	12596		Infiltration	Area	5000	¼ Air Change	0.32	320000
Ceiling	2500		No Insulation	11	27500			Ht.	200
Floor	5000		No Insulation	4	20000		Heat Loss Subtotal					682262
Infiltration	Area	5000	¼ Air Change	0.068	68000		Total Loss	682262		1.25		852827.5
	Ht.	200
People	300		300		90000
Appliance	2000				2000		Notes:
Subtotal					342357
Duct Loss	342357		0.05		17117.85
Total Sensible					359474.85
Latent Infiltration	Area	5000	¼ Air Change	0.065	65000
	Ht.	200
People	300		230		69000
Total Latent					134000
Total Gain	359474.85		134000		493474.85

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1