## Sheet1
Scoville – Heat Gain/Loss Calculator

Job Name:	SmokeTest5					Customer:	John Q. Sample
Job Number:	0					Address:	520 North Main St.
Date:					Meadville, PA 16335

	Area		CM		Gain			Area		HM		Loss
Gross Wall	200					Gross Wall	200
North Window	2		15		30		Windows	5		Single	80	400
South Window	3		25		75		Doors	3		Single	80	240
East/West Window	0		45		0		Net Wall	192		2 Inches	7	1344
Sky-Lite	0		139		0		Ceiling	1500		No Insulation	21	31500
Doors	3		11		33		Floor	1500		Crawl Space	21	31500
Net Wall	192		2 Inches	2	384		Infiltration	Area	1500	¼ Air Change	0.32	4320
Ceiling	1500		No Insulation	11	16500			Ht.	9
Floor	1500		No Insulation	4	6000		Heat Loss Subtotal					69304
Infiltration	Area	1500	¼ Air Change	0.068	918		Total Loss	69304		1.25		86630
	Ht.	9
People	5		300		1500
Appliance	2000				2000		Notes:
Subtotal					27440
Duct Loss	27440		0.05		1372
Total Sensible					28812
Latent Infiltration	Area	1500	¼ Air Change	0.065	877.5
	Ht.	9
People	5		230		1150
Total Latent					2027.5
Total Gain	28812		2027.5		30839.5

(Input cells are highlighted in yellow)
(Questionable cells are highlighted in blue)
(Output cells are highlighted in green)

## Sheet2
Heating/Cooling Multipliers

Wall CM			Windows/Door HM
No Insulation	4		Single	80
2 Inches	2		Insulated	48
3 Inches	1.5		Storm	40
[Custom]	1		Triple	23
			[Custom]	1
Ceiling CM
No Insulation	11		Ceiling HM
3 Inches	3.2		No Insulation	21
6 Inches	2.1		3 Inches	6
10 Inches	1.3		6 Inches	4
[Custom]	1		10 Inches	2
			[Custom]	1
Floors CM
No Insulation	4		Floor HM
3 Inches	0.8		Crawl Space	21
6 Inches	0.5		Crawl – Ins.	5
[Custom]	1		Base – No Ins.	4
			Bsmt. – 3 Inches	2
Windows			[Custom]	1
North	15
South	25		Wall HM
East/West	45		No Insulation	18
Skylight	139		2 Inches	7
Doors	11		3 Inches	5
[Custom]	1		6 Inches	4
			[Custom]	1
Infiltration
1 Air Change	0.275		Infiltration HM
½ Air Change	0.137		1 Air Change	1.26
¼ Air Change	0.068		¾ Air Change	0.95
[Custom]	1		½ Air Change	0.63
			¼ Air Change	0.32
Latent Heat Inf.			[Custom]	1
1 Air Change	0.26
½ Air Change	0.13		Slab/Grade
¼ Air Change	0.065		No Insulation	56.7
[Custom]	0.068		1.5 Inches	28.7
			[Custom]	1

			Slab with Perm
			No Insulation	133
			1.5 Inches	79.8
			Custom	1